## Common Data
ENTSO-E Market Modelling Database
| Category # | Fuel | Type | Efficiency range in NCV terms | Standard efficiency in NCV terms | CO2 emission factor | Variable O&M cost | Min Time on | Min Time off | Start-up fuel consumption - warm start | Start-up fix cost (e.g. wear) warm start | Start-up fuel consumption - cold start | Start-up fix cost (e.g. wear) cold start | Start-up fuel consumption - hot start | Start-up fix cost (e.g. wear) hot start
|  |  |  | % | % | kg / Net GJ | €/MWh | hours | hours | Net GJ /MW. start | € /MW. start | Net GJ /MW. start | € /MW. start | Net GJ /MW. start | € /MW. start | Transition time [h] from hot to warm | Transition time [h] from hot to cold
| 1 | Nuclear | - | 30% - 35% | 33% | 0 | 9 | 12 | 12 | 14 | 21
| 2 | Hard coal | old 1 | 30% - 37% | 35% | 94 | 3.3 | 8 | 8 | 18 | 69.69 | 21 | 93.97 | 10.5 | 49.33 | 12 | 72
| 3 | Hard coal | old 2 | 38% - 43% | 40% | 94 | 3.3 | 6 | 6 | 18 | 50.12 | 21 | 81.44 | 10.5 | 42.29 | 12 | 72
| 4 | Hard coal | new | 44% - 46% | 46% | 94 | 3.3 | 5 | 5 | 18 | 42.29 | 21 | 57.17 | 10.5 | 30.54 | 12 | 72
| 5 | Hard coal | CCS | 30% - 40% | 38% | 9.4 | 6.6 | 7 | 7 | 18 | 50.12 | 21 | 81.44 | 10.5 | 42.29 | 12 | 72
| 6 | Lignite | old 1 | 30% - 37% | 35% | 101 | 3.3 | 11 | 11 | 18 | 69.69 | 21 | 93.97 | 10.5 | 49.33 | 12 | 72
| 7 | Lignite | old 2 | 38% - 43% | 40% | 101 | 3.3 | 9 | 9 | 18 | 50.12 | 21 | 81.44 | 10.5 | 42.29 | 12 | 72
| 8 | Lignite | new | 44% - 46% | 46% | 101 | 3.3 | 8 | 8 | 18 | 42.29 | 21 | 57.17 | 10.5 | 30.54 | 12 | 72
| 9 | Lignite | CCS | 30% - 40% | 38% | 10.1 | 6.6 | 10 | 10 | 18 | 50.12 | 21 | 81.44 | 10.5 | 42.29 | 12 | 72
| 10 | Gas | conventional old 1 | 25% - 38% | 36% | 57 | 1.1 | 5 | 5 | 7.6 | 68.13 | 9.7 | 69.69 | 4.1 | 32.89 | 8 | 48
| 11 | Gas | conventional old 2 | 39% - 42% | 41% | 57 | 1.1 | 5 | 5 | 7.6 | 45.42 | 9.7 | 58.73 | 4.1 | 28.19 | 8 | 48
| 12 | Gas | CCGT old 1 | 33% - 44% | 40% | 57 | 1.6 | 3 | 3 | 7.6 | 72.83 | 9.7 | 79.09 | 4.1 | 43.85 | 8 | 48
| 13 | Gas | CCGT old 2 | 45% - 52% | 48% | 57 | 1.6 | 3 | 3 | 7.6 | 43.07 | 9.7 | 61.86 | 4.1 | 27.41 | 8 | 48
| 14 | Gas | CCGT present 1 | 53% - 60% | 56% | 57 | 1.6 | 2 | 2 | 7.6 | 25.06 | 9.7 | 36.02 | 4.1 | 21.93 | 8 | 48
| 15 | Gas | CCGT present 2 | 53% - 60% | 58% | 57 | 1.6 | 2 | 2 | 7.6 | 25.06 | 9.7 | 36.02 | 4.1 | 21.93 | 8 | 48
| 16 | Gas | CCGT new | 53% - 60% | 60% | 57 | 1.6 | 2 | 2 | 7.6 | 25.06 | 9.7 | 36.02 | 4.1 | 21.93 | 8 | 48
| 17 | Gas | CCGT CCS | 43% - 52% | 51% | 5.7 | 3.2 | 4 | 4 | 7.6 | 43.07 | 9.7 | 61.86 | 4.1 | 27.41 | 8 | 48
| 18 | Gas | OCGT old | 35% - 38% | 35% | 57 | 1.6 | 1 | 1 | 0.21 | 52.47 | 0.25 | 52.47 | 0.2 | 30.54 | 2 | 3
| 19 | Gas | OCGT new | 39% - 44% | 42% | 57 | 1.6 | 1 | 1 | 0.21 | 20.36 | 0.25 | 24.28 | 0.2 | 17.23 | 2 | 3
| 20 | Light oil | - | 32% - 38% | 35% | 78 | 1.1 | 1 | 1 | 0.21 | 36 | 0.25 | 38.4 | 0.2 | 24 | 2 | 3
| 21 | Heavy oil | old 1 | 25% - 37% | 35% | 78 | 3.3 | 3 | 3 | 7.6 | 70 | 9.7 | 93.97 | 4.1 | 49.33 | 8 | 48
| 22 | Heavy oil | old 2 | 38% - 43% | 40% | 78 | 3.3 | 3 | 3 | 7.6 | 50 | 9.7 | 81.44 | 4.1 | 42.29 | 8 | 48
| 23 | Oil shale | old | 28% - 33% | 29% | 100 | 3.3 | 11 | 11 | 18 | 60 | 21 | 88 | 10.5 | 46 | 12 | 72
| 24 | Oil shale | new | 34% - 39% | 39% | 100 | 3.3 | 8 | 8 | 18 | 42 | 21 | 57.17 | 10.5 | 31 | 12 | 72
| 25 | Hydrogen | Fuel cell | 34% - 60% | 60% | 0 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 26 | Hydrogen | CCGT | 53% - 60% | 60% | 0 | 1.6 | 2 | 2 | 7.6 | 25.06 | 9.7 | 36.02 | 4.1 | 21.93 | 8 | 48
| 27 | Hydrogen | OCGT | 39% - 44% | 42% | 0 | 1.6 | 1 | 1 | 0.21 | 20.36 | 0.25 | 24.28 | 0.2 | 17.23 | 2 | 3
| Category # | Fuel | Type | Unavailability |  |  |  | Minimum stable generation | Ramp up rate | Ramp down rate | Fixed generation reduction
|  |  |  | Forced outage |  | Planned outage
|  |  |  | annual rate | Mean time to repair | annual rate | winter
|  |  |  | % | Days | number of days | % of annual number of days | (% of max power) | % of max output power / min | % of max output power / min | % of max output power
| 1 | Nuclear | - | 5% | 7 | 54 | 15% | 40% | 5% | 5% | 0%
| 2 | Hard coal | old 1 | 10% | 1 | 27 | 15% | 40% | 2% | 5% | 0%
| 3 | Hard coal | old 2 | 10% | 1 | 27 | 15% | 40% | 2% | 5% | 0%
| 4 | Hard coal | new | 7.5% | 1 | 27 | 15% | 25% | 4% | 5% | 0%
| 5 | Hard coal | CCS | 7.5% | 1 | 27 | 15% | 25% | 4% | 5% | 0%
| 6 | Lignite | old 1 | 10% | 1 | 27 | 15% | 50% | 2% | 5% | 0%
| 7 | Lignite | old 2 | 10% | 1 | 27 | 15% | 50% | 2% | 5% | 0%
| 8 | Lignite | new | 7.5% | 1 | 27 | 15% | 50% | 2% | 5% | 0%
| 9 | Lignite | CCS | 7.5% | 1 | 27 | 15% | 50% | 2% | 5% | 0%
| 10 | Gas | conventional old 1 | 8% | 1 | 27 | 15% | 20% | 15% | 15% | 0%
| 11 | Gas | conventional old 2 | 8% | 1 | 27 | 15% | 20% | 15% | 15% | 0%
| 12 | Gas | CCGT old 1 | 8% | 1 | 27 | 15% | 50% | 2% | 5% | 0%
| 13 | Gas | CCGT old 2 | 8% | 1 | 27 | 15% | 50% | 2% | 5% | 0%
| 14 | Gas | CCGT present 1 | 5% | 1 | 27 | 15% | 40% | 4% | 5% | 0%
| 15 | Gas | CCGT present 2 | 5% | 1 | 27 | 15% | 40% | 4% | 5% | 0%
| 16 | Gas | CCGT new | 5% | 1 | 27 | 15% | 40% | 4% | 5% | 0%
| 17 | Gas | CCGT CCS | 5% | 1 | 27 | 15% | 40% | 4% | 5% | 0%
| 18 | Gas | OCGT old | 8% | 1 | 13 | 15% | 50% | 8% | 8% | 0%
| 19 | Gas | OCGT new | 5% | 1 | 13 | 15% | 40% | 12% | 12% | 0%
| 20 | Light oil | - | 8% | 1 | 13 | 15% | 50% | 8% | 8% | 0%
| 21 | Heavy oil | old 1 | 10% | 1 | 27 | 15% | 50% | 8% | 8% | 0%
| 22 | Heavy oil | old 2 | 10% | 1 | 27 | 15% | 50% | 8% | 8% | 0%
| 23 | Oil shale | old | 10% | 1 | 27 | 15% | 50% | 8% | 8% | 0%
| 24 | Oil shale | new | 7.5% | 1 | 27 | 15% | 50% | 8% | 8% | 0%
| 25 | Hydrogen | Fuel cell | 2.5% | 1 | 7 | 0% | 0% | 0% | 0% | 0%
| 26 | Hydrogen | CCGT | 5% | 1 | 27 | 15% | 40% | 4% | 5% | 0%
| 27 | Hydrogen | OCGT | 5% | 1 | 13 | 15% | 40% | 12% | 12% | 0%